## Slide 1: Master’s Thesis Defence
Modelling and Performance Investigation of a Bifacial Agrivoltaic Installation in Foulum

## Slide 2: Agenda
Introduction
  Bifacial configurations
  Methodology of the project
The PV systems
  Overview of system
  Sensors
Data for comparison
  Data outages
  Limits for inclusion
The Performance model
  Transposition modelling
  Module modelling
  Inverter modelling
Results
  Plane Of Array Irradiance
  AC Power
  System efficiencies
Conclusion
How do vertical east-west and south-oriented PV modules perform in an agrivoltaic installation?
How does the modelling of the performance compare with experimental measurements?
What are the most relevant parameters to be measured and the best modelling approaches to improve the fitting?
1
2
3
4
5
6
?
?
?

## Slide 3: Introduction – Bifacial configurations
Source:Radovan Kopecek and Joris Libal. “Towards large-scale deployment of bifacial photovoltaics”. In: Nature Energy 3.6 (June 2018), pp. 443–446. issn: 2058-7546. doi: 10.1038/s41560- 018-0178-0. url: https://doi.org/10.1038/s41560-018-0178-0.
Silicon PV market is dominated by bifacial cell technology
Different generation profile -> potentially reducing balancing needs
Dual land use -> food and electricity production
Agrivoltaic installations can be used as windbreaks -> potentially increasing the yield

## Slide 4: Methodology overview

## Slide 5: The pv installation

## Slide 6
REF. Cell
REF. Cell
2*REF. Cell
Weather station
E
W
S
N

## Slide 7: On-site measurements
Provides the input for the Performance Model and comparisons
Reference cells are not affected by shadows from the structure
5-minute resolution

## Slide 8: Data for comparison
Clear sky and cloudy conditions
Data outages
Both long intervals and individual days
One long interval from four short – 101 days
Comparison limits

## Slide 9: The Performance Model
From astronomy to energy

## Slide 10: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 11: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 12: Dni model
Geometry model using GHI and DHI
Empirical models using only GHI
Solar radiation beam transmittance based on clear-sky model clearness index
Horizontal extraterrestrial irradiance
Empirical models has skewness
Simple geometry more symmetric

## Slide 13: Dni model
Geometry model using GHI and DHI
Empirical models using only GHI
Solar radiation beam transmittance based on clear-sky model clearness index
Horizontal extraterrestrial irradiance
Empirical models has skewness
Simple geometry more symmetric

## Slide 14: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 15: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 16: Albedo
2024-01-16
2023-08-10
2024-01-25
2023-08-14

## Slide 17: albedo
Average of midday
No seasonal variation
Snow increases the albedo

## Slide 18: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 19: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 20: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 21: Transposition - One row approach
Three main components
Direct – solar geometry
Sky diffuse – sky model
Ground diffuse – isotropic
Transposition factors - isotropic

## Slide 22: One row approach – sky models
+
circumsolar
isotropic
isotropic
circumsolar
horizon
is the circumsolar coefficient
is the horizon brightening coefficient
HayDavies: Introduces diffuse circumsolar irradiance
PEREZ: Introduces diffuse horizon brightening irradiance

## Slide 23: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 24: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 25: Transposition – shadows - infinite sheds
Infinitely many infinite rows – neglect edge effects
Only isotropic and haydavies sky model
Returns the average irradiance of the module
Adjustments to the one row approach

## Slide 27: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 28: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 29: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 30: Spectral mismatch modifier
Accounts for absorption of solar radiation in the atmosphere
The coefficients depend on the cell technology
Effective plane of array irradiance
Sandia modifier
Gueymard modifier

## Slide 31: Spectral mismatch modifier
Best fit model:
Gueymard
Best fit model:
None
Best fit model:
Gueymard
Best fit model:
None

## Slide 32: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 33: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 34: Incidence angle modifier
Adapted from: https://www.pvsyst.com/help/iam_loss.htm
Reflections due to the difference in refractive index
I-V characteristics are obtained at STC (normal irradiance) and are a result of the the reflections -> only need to account for incidence angles different from normal.
Fresnel equations for normal irradiance
Sky diffuse

## Slide 35: Incidence angle modifier
Best fit model:
SAPM

## Slide 36: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 37: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 38: Single diode model
The basic idea
The single diode model
I-V characteristics at different temperatures
Method
I-V characteristics at different irradiations
Estimate SDM parameters at STC from data sheet
Calculate SDM parameters at EPOAI
Calculate MPP
Simple relation for MPP

## Slide 39: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 40: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 41: Temperature model
Sandia Array Performance Model
Pvsyst – constant heat transfer
Cell temperature
Module temperature
Cell temperature

## Slide 42: Temperature model
Sandia Array Performance Model
Pvsyst – constant heat transfer
Cell temperature
Module temperature
Cell temperature

## Slide 43: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 44: The model chain
Transposition - Simple
Shadow model
Transposition Model
Module Model
Inputs to model

## Slide 45: INVERTER MODEL
Inverter efficiency depend on the load
Sandia Model vs Logarithmic fit
Tilted inverter low efficiency at low temperature – snow?
Sandia Model

## Slide 46: INVERTER MODEL
Inverter efficiency depend on the load
Sandia Model vs Logarithmic fit
Tilted inverter low efficiency at low temperature – snow?
Sandia Model

## Slide 47: Results
The effective irradiance and AC power with the optimized performance model

## Slide 48: Resulting irradiance - Tilted
Good prediction of upward facing side most of 05-12.
Over prediction of downward facing side in the afternoon 05-12 -> over predicts total.
Slight under prediction of upward facing side in the morning of 05-11.
Good prediction of downward facing side of 05-11.

## Slide 49: Resulting irradiance - Vertical
The model under predicts the irradiance in the morning of 05-17 and 05-12.
The model over predicts the irradiance in the afternoon of 05-12.
Good prediction in overcast conditions on 05-11.

## Slide 50: AC power generation
Effects of shadows from structure in vertical generation in the morning of 05-12.
Slightly over prediction of generation in afternoon of 05-12 for vertical.
Inverter clipping of tilted generation on 05-12.
Small effects of shadows from structure and no inverter clipping in overcast conditions.

## Slide 51: Evaluation of the Performance Model
Chart: Comparison results for the data points
| Tilted up | Tilted down | East | West | Tilted Electricity | Vertical Electricity
Sensor error | 7.7 | 7.7 | 7.7 | 7.7
DNI model | 13 | 73.3 | 25.2 | 15
GHI sensor | 10.4 | 93 | 20.1 | 21.6
Transposition | 10.4 | 49.1 | 11.1 | 15.2
IAM | 10.3 | 44.4 | 11.2 | 11.6
Spectral modifier | 10.3 | 43.4 | 10.5 | 11.6
DC | 19.6 | 23.8
AC | 18.9 | 22.1

## Slide 52: Evaluation of the Performance Model
Chart: Comparison results for the data points
| Tilted up | East | West | Tilted Electricity | Vertical Electricity
Sensor error | 7.7 | 7.7 | 7.7
DNI model | 13 | 25.2 | 15
GHI sensor | 10.4 | 20.1 | 21.6
Transposition | 10.4 | 11.1 | 15.2
IAM | 10.3 | 11.2 | 11.6
Spectral modifier | 10.3 | 10.5 | 11.6
DC | 19.6 | 23.8
AC | 18.9 | 22.1
Chart: AC Energy generation over the long interval
| Tilted | Vertical
AC modelled | 7068.5 | 6357.2
AC measured | 6792.7 | 4727.27
High errors on downward facing side
5-minute resolution
GHI sensor increases error for the west side
IAM only really improves the west side
Spectral modifiers gives almost no improvements
Comparisons for electricity is with the noon excluded
AC energy generation for all times the inverters are operating.
The model overestimates the AC generation with 4.1% and 34.5% for tilt and vertical respectively

## Slide 53: System efficiency
Can reach similar levels
Vertical lower in cloudy conditions - structure affects all day
Vertical low in morning with sun
Inverter clipping
Snow affects the tilted installation
System efficiency

## Slide 54: conclusion
Reaches similar system efficiencies in parts of the days just below 20%.
The efficiencies are highly influenced by the structure and inverter clipping.
Vertical generates 30% AC energy less than the tilted over the long interval.
How do vertical east-west and south-oriented PV modules perform in an agrivoltaic installation?
How does the modelling of the performance compare with experimental measurements?
What are the most relevant parameters to be measured and the best modelling approaches to improve the fitting?
Predicts AC generation from vertical to be 10% less than tilted vs. 30% measured.
Best fit EPOAI model nRMSEs 10.3% and 11.6% (tilt, vertical)
Best fit AC power model nRMSEs 18.9% and 22.1% (tilt, vertical)
The model overestimates the AC generation with 4.1% and 34.5% for tilt and vertical respectively.
Large reductions in nRMSE when using both GHI and DHI for DNI.
14.1% and 16.7% (tilt, vertical) of insolation comes from ground reflected irradiance – albedo measurements should be improved.
Model shadow effects from structure on the east side.
More reference cells, relocation of exciting and thermocouples of cells to make a better comparison between modelled and measured.

## Slide 56
REF. Cell
REF. Cell
2*REF. Cell
New loc. REF. Cell
New loc. REF. Cell
2*New loc. REF. Cell
New REF. Cell
New REF. Cell
2*New
REF. Cell

## Slide 57: The comparison plots
Modelled vs Measured Effective Plane Of Array Irradiance